## Floor Plans
Main Floor

## HVAC Drawings
Attic
Basement
TODO

## Loads
See Reports

## Blocks
System/Block Name | Heating air flow | Heating Load | Heating Capacity | AFUE | Motor | Stages | Cooling air flow | Cooling Load | Cooling Capacity | SEER2 | Motor
Basement Furnace | 2000 | 80199.9 | 100000 | 0.8 | Variable | 2 Stage | 1600 | 44761 | 48000 | 15 | Variable
Attic Furnace | 1600 | 51635 | 75000 | 0.8 | Variable | 2 Stage | 1400 | 39104.9 | 42000 | 15 | Variable
total | 3600 | 131834.9 | 175000 |  |  |  | 3000 | 83865.9 | 90000
Reference Model
R802V | https://files.myrheem.com/webpartners/ProductDocuments/A4C9EC3A-CF82-477B-8143-1273C1F28365.pdf
https://www.rheem.com/group/rheem-gas-furnaces-prestige-series-up-to-80-afue-variable-speed-upflow-horizontal-r802v/?Fuel%20Type=Natural%20Gas

## Rooms
Room Name | Floor | System/Block | Zone | Floor Area | Volume | Room Type | Number of Occupants | Heating Load | Heating Fraction | Heating CFM | Sens Cooling Load* | Cooling Fraction | Cooling CFM | Duct Size CFM
Basement West | 1 | Basement Handler | Zone | 135 | 1078 | Basement Unfinished | 0 | 18802 | 0.234 | 703 | 5910 | 0.137 | 219 | 703
Basement East | 1 | Basement Handler | Zone | 96 | 770 | Basement Unfinished | 0 | 14808 | 0.185 | 554 | 4664 | 0.108 | 173 | 554
Living | 2 | Basement Handler | Zone | 286 | 2576 | Other | 1 | 12915 | 0.161 | 483 | 11151 | 0.258 | 413 | 483
Front Bedroom | 2 | Basement Handler | Zone | 155 | 1397 | Bedroom | 1 | 4890 | 0.061 | 183 | 2629 | 0.061 | 97 | 183
Front Stairs | 2 | Basement Handler | Zone | 55 | 495 | Other | 0 | 4460 | 0.056 | 167 | 1698 | 0.039 | 63 | 167
Dining | 2 | Basement Handler | Zone | 176 | 1580 | Other | 1 | 5045 | 0.063 | 189 | 2098 | 0.049 | 78 | 189
Bathroom | 2 | Basement Handler | Zone | 42 | 378 | Other | 0 | 2024 | 0.025 | 76 | 1098 | 0.025 | 41 | 76
Kitchen | 2 | Basement Handler | Zone | 155 | 1395 | Kitchen | 1 | 2949 | 0.037 | 110 | 3579 | 0.083 | 132 | 132
Back stairs | 2 | Basement Handler | Zone | 75 | 675 | Other | 0 | 1538 | 0.019 | 58 | 442 | 0.01 | 16 | 58
Mainfloor Closets | 2 | Basement Handler | Zone | 20 | 180 | Other | 0 | 69 | 0.001 | 3 | 10 | 0 | 0 | 3
Back Bedroom | 2 | Basement Handler | Zone | 175 | 1575 | Other | 0 | 9393 | 0.117 | 351 | 7030 | 0.163 | 260 | 351
Laundry | 2 | Basement Handler | Zone | 75 | 675 | Other | 0 | 3243 | 0.04 | 121 | 2877 | 0.067 | 106 | 121
Up Bathroom | 3 | Attic Handler | Zone | 42 | 378 | Other | 0 | 1950 | 0.038 | 76 | 1256 | 0.032 | 45 | 76
Up Laundry / Hallway | 3 | Attic Handler | Zone | 155 | 1395 | Other | 0 | 2393 | 0.046 | 93 | 1222 | 0.031 | 44 | 93
Up Front Bedroom | 3 | Attic Handler | Zone | 162 | 1458 | Bedroom | 1 | 4477 | 0.087 | 173 | 3125 | 0.08 | 112 | 173
Gameroom | 3 | Attic Handler | Zone | 207 | 1865 | Other | 1 | 6332 | 0.123 | 245 | 3472 | 0.089 | 124 | 245
Upstairs closets | 3 | Basement Handler | Zone | 20 | 180 | Other | 0 | 63 | 0.001 | 2 | 54 | 0.001 | 2 | 2
Second Master | 3 | Attic Handler | Zone | 175 | 1575 | Bedroom | 0 | 10199 | 0.198 | 395 | 8106 | 0.207 | 290 | 395
Master | 3 | Attic Handler | Zone | 271 | 2441 | Bedroom | 0 | 13086 | 0.253 | 507 | 12253 | 0.313 | 438 | 507
Master Closet | 3 | Attic Handler | Zone | 32 | 284 | Other | 0 | 3080 | 0.06 | 119 | 2586 | 0.066 | 92 | 119
Up Back Bedroom | 3 | Attic Handler | Zone | 184 | 1654 | Bedroom | 1 | 10118 | 0.196 | 392 | 7187 | 0.183 | 257 | 392
|  |  |  | 2692.75 | 24003.75 |  |  | 131834 | 2.001 |  | 82447 | 2.002

## Attic Ducts
SB Number | Room Served | AirFlow CFM | Friction Rate | Diameter Inches | Rect Height Inches | Length Feet | Velocity FPM | Register Size (in) | Trunk # | Return # | Type
SB 14.1 | Up Bathroom | 60 | 0.1 | 5 | N/A | 4' | 443 | 12 x 6 | ST1 | Dir Return 1(---) | Flex Duct R6
SB 15.1 | Up Laundry / Hallway | 74 | 0.1 | 5 | N/A | 4' | 543 | 10 x 10 | ST2 | Dir Return 1(---) | Flex Duct R6
SB 16.1 | Up Front Bedroom | 139 | 0.1 | 7 | N/A | 8' | 519 | 12 x 12 | ST1 | Dir Return 2(---) | Flex Duct R6
SB 17.1 | Gameroom | 98 | 0.1 | 6 | N/A | 9' | 500 | 10 x 10 | ST2 | Dir Return 2(---) | Flex Duct R6
SB 17.2 | Gameroom | 98 | 0.09 | 6 | N/A | 19' | 500 | 10 x 10 | ST2 | Dir Return 2(---) | Flex Duct R6
SB 19.1 | Second Master | 158 | 0.1 | 7 | N/A | 17' | 591 | 12 x 12 | ST1 | Dir Return 1(---) | Flex Duct R6
SB 19.2 | Second Master | 158 | 0.1 | 7 | N/A | 13' | 591 | 12 x 12 | ST1 | Dir Return 1(---) | Flex Duct R6
SB 20.1 | Master | 146 | 0.09 | 7 | N/A | 29' | 546 | 12 x 12 | ST1 | Dir Return 2(---) | Flex Duct R6
SB 20.2 | Master | 146 | 0.09 | 7 | N/A | 19' | 546 | 12 x 12 | ST1 | Dir Return 2(---) | Flex Duct R6
SB 20.3 | Master | 146 | 0.09 | 7 | N/A | 28' | 546 | 12 x 12 | ST1 | Dir Return 2(---) | Flex Duct R6
SB 21.1 | Master Closet | 96 | 0.09 | 6 | N/A | 23' | 486 | 10 x 10 | ST2 | Dir Return 2(---) | Flex Duct R6
SB 22.1 | Up Back Bedroom | 157 | 0.1 | 7 | N/A | 13' | 587 | 12 x 12 | ST2 | Dir Return 1(---) | Flex Duct R6
SB 22.2 | Up Back Bedroom | 157 | 0.1 | 7 | N/A | 8' | 587 | 12 x 12 | ST2 | Dir Return 1(---) | Flex Duct R6
ST Number | --- | AirFlow CFM | Friction Rate | Diameter Inches | Rect Height Inches | Length Feet | Velocity FPM | --- | Trunk # | --- | Type
ST1 | --- | 953 | 0.09 | 16 x 12 | 12",9'" | 715 | --- | handler | --- | --- | Metal
ST2 | --- | 679 | 0.09 | 16 x 12 | 12",6'" | 510 | --- | handler | --- | --- | Metal
RB Number | Location | AirFlow CFM | Friction Rate | Diameter Inches | Rect Height Inches | Length Feet | Velocity FPM | Grille Size (inches) | Trunk # | --- | Type
Dir Return 1 |  | 764 | 0.07 | 21 x 14 | 4 | 4 | 374 | 21 x 14 | handler | --- | Metal
Dir Return 2 |  | 868 | 0.07 | 21 x 14 | 4 | 6 | 425 | 21 x 14 | handler | --- | Metal